|  | KJF205 |
| --- | --- |
| AIRREX ASHRAE Grade W-Cell Extended Surface Air Filter is a Separator-type air filter which is designed for any commercial or industrial HVAC systems use, required medium to high efficiency. Per ASHRAE 52.1-1992 standard, W-Cell filters have an average atmospheric dust spot efficiency range 60-65%, 80-85% and 90-95% (in NBS Test Method); per ASHRAE 52.2, the efficiency is MERV11, MERV12 & MERV14. Operating face velocity ranges are from 0-375FPM (0-1.9m/sec) for 6 inch (150mm) deep filters, and from 0-625FPM (0-3.175m/sec) for 12inch (295mm) deep units. Air filtration system which was originally supplied by other equipment manufacturers can be replaced by W-Cell to improve air cleaning performance and enhance reliability. | ASHRAE Grade W-Cell Extended Surface Air Filter 中性能W-Cell型空氣濾網 Testing Method 測試方法 Dot Spot Efficiency (in NBS Testing Method) 比色法 Arrestance (in AFI Testing Method) 比重法 MERV 90~95% > 99% 14 80~85% > 98% 13 60~65% > 97% 11 By ASHRAE Standard 52.1-1992 (Equal to EN 779) 依ASHRAE 52.1-1992標準 (德國EN 779) By ASHRAE 52.2-1999 Standard 依 ASHRAE 52.2-1999標準 *High temperature resistance filter is available for special use. *依特殊使用性質，可製成耐高溫濾網 Features: Both edges of aluminum separators are rolled to prevent media tearing and provide maximum integrity. Rolled edges can also reduce the injury of cutting worker's hands during installation. For special use, high temperature resistance filter is available for 750 FPM use. Ultra-Fine Glass Fiber Media: W-Cell Media is manufacture from glass microfiber. The media is water-resistant and can withstand temperature up to 350℃. Fire-Retardant Sealant: Filter element is completely sealed around with fire-retardant epoxy, polyurethane form or silicon sealant. |

KJF 205

Face Guard: A Metal hardware close faceguard installed on both sides of the filter is available as an option. Temperature: Standard units are rated for maximum 200℉. Temperature up to 750℉ can be obtained by optional sealants, gaskets and frames. Outer Frame: The frame is available for Wooden Frame (Fire-Retardant Particle Board Frame) and Metal Frame (Galvanized Steel, Aluminum and Stainless Steel) in box type or header type. High Density Fire-Retardant Particle Board Frame is an unique construction to ensure maximum rigidity of filter. 特色：中性能W-CELL型為波浪隔板型，雙摺邊鋁隔板避免濾材被插破，亦可降低安裝時被割傷的潛在危險。 依特殊使用性質，可製成耐高溫型濾網，可在750呎/分之表面風速下使用。 效率：依ASHRAE 52.1-1992標準法測試，濾網具比色法效率60-65%、80-85%、90-95%可供選擇。 濾材：是由超細玻璃纖維所製，此濾材具防水性且能耐溫至350℃。濾網四周可選用耐火之環氧樹脂或PU膠密封，外框與濾材無洩漏之虞。 外框：框材可選用木框、鍍鋅鐵框、鋁框或不銹鋼框。

KJF 205

Performance Data – ASHRAE Grade W-Cell Extended Surface Air Filter 中效率濾網性能表 - W-Cell型空氣濾網 Efficiency Nominal Size Actual Size Rated Capacity Pressure Drop 效率 通稱尺寸 實際尺寸 額定風量 壓力損失 （％） (W*H*D) (W*H*D) （CMH） （Pa） Dot Spot Efficiency (in NBS) 比色法 Arrestance (in AFI) 比重法 （inch） （mm） Initial Resistance 初壓損 Final Resistance 末壓損 90~95 ＞ 99 12*24*6 289*595*150 850 82 324 24*24*6 595*595*150 1700 12*24*12 289*595*292 1700 137 24*24*12 595*595*292 3400 80~85 ＞ 98 12*24*6 289*595*150 850 74 324 24*24*6 595*595*150 1700 12*24*12 289*595*292 1700 120 24*24*12 595*594*292 3400 60~65 ＞ 97 12*24*6 289*595*150 850 62 324 24*24*6 595*595*150 1700 12*24*12 289*595*292 1700 102 24*24*12 595*595*292 3400 1. Recommended Final Resistance on all S Series Filters is 1.5” w.g. 2. Special Sizes are available upon request. ※特殊規格可生產製造

KJF 205

Material and Service Conditions 材質和使用條件 Type 型式 Description 說明 Construction 總成 Media 濾材 Ultra-Fine Glass Fiber 超細玻璃纖維濾紙 Support Grid 支撐材 Corrugated Aluminum Separator 波浪隔板 Sealant 密封膠 PU BASE Gasket Material 墊片材質 Neoprene Rubber 新平橡膠 Frame Material 外框材質 Wooden Frame 木框 Metal Frame 金屬框 Frame Type 外框型式 Box Type 箱型 Single Header 單法蘭 Service Conditions 使用條件 The maximum continuous use temperature 連續使用最高溫度 ℃ 60 Instant Highest Humidity 使用瞬間最高濕度 % RH 100（No condensation state） 100（無結露狀態下） 名 稱:康智富科技有限公司 統 編:29168436 地 址:新北市永和區仁愛路141巷30弄26號1樓 電 話:+886-2-29256286 傳 真:+886-2-29256096 E-MAIL :ks.best@msa.hinet.net