|  | KJF206 |
| --- | --- |
| P-Cell Air Filter is the most saving space air filter (only 4” thickness). It is thinner & lighter, but with high performance of air filtration. P-Cell is the best choice for HVAC system. It is ideal for new installations, as it is smaller to be able to save air handling unit’s space & cost. | ASHRAE Grade P- Cell Extended Surface Air Filter 中性能P-Cell型空氣濾網 Testing Method 測試方法 Dot Spot Efficiency (in NBS Testing Method) 比色法 Arrestance (in AFI Testing Method) 比重法 MERV 90~95% > 99% 14 80~85% > 98% 13 60~65% > 97% 11 By ASHRAE Standard 52.1-1992 (Equal to EN 779) 依ASHRAE 52.1-1992標準 (德國EN 779) By ASHRAE 52.2-1999 Standard 依ASHRAE 52.2-1999標準 Features: P-Cell Air Filter is made by mini-pleats to enlarge the media filtration area. Although the thickness is only 4”, it can make air flow rate 2000 CFM by size 24”x24”. Compare with other medium efficiency air filters, P-Cell air filter has better performance in pressure drop. Efficiency: Per ASHRAE 52.1-1992 standard, the filters have an average atmospheric dust spot efficiency range 60-65%, 80-85% and 90-95% (in NBS Test Method); per ASHRAE 52.2, the efficiency is MERV11, MERV12 & MERV14. |

KJF 206

Media: P-Cell media is manufactured from Water-Resistant Glass Microfiber and Synthetic Fiber. The glass microfiber paper is formed with a dual density construction, coarser fiber is formed on the upstream and finer fiber is formed on the downstream. This structure can increase media’s dust collection capacity. The Synthetic Fiber is made of meltblown microfiber offering maximum dust collection capacity. P-Cell media is pleated form the filter pack and use hot melting glue to replace the traditional aluminum separators. It is without the aluminum separators or expanded metal to support the media, but ensure the maximum air flow and minimum resistance to enhance the dust collection capacity. Outer Frame: The frame is available for Paper and Metal Frame (Galvanized Steel, Aluminum and Stainless Steel). Paper frame consists of two-pieces of moisture-resistant press paper. Tow press papers are bonded together to comprise a double wall frame, and the media pack is just stick closely with this double wall frame. 特色：ASHRAE級中性能P-CELL型濾網僅4吋厚，設計上由迷你摺紙方式製成，過濾面積也較大，由於較 可縮小空調箱體積及成本。 效率：依ASHRAE 52.1-1992標準法測試，濾網具比色法效率60-65%、80-85%、90-95%可供選擇。 濾材：防水玻璃纖維紙，雙層密度結構粗纖維於上風處，細纖維於下風處，此結構讓濾材增加容塵量。濾材摺紙成型塊，無鋁製隔板或無擴張網支撐濾材，以上膠黏合成型，適用於大風量，達到高補集率效果。 外框：框材可選用紙框、鍍鋅鐵框、鋁框或不銹鋼框。

KJF 206

Performance Data – ASHRAE Grade P-Cell Extended Surface Air Filter 中效率濾網性能表 – P-Cell型空氣濾網 Efficiency Nominal Size Actual Size Rated Capacity Pressure Drop 效率 通稱尺寸 實際尺寸 額定風量 壓力損失 （％） （W*H*D） （W*H*D） （CMH） （Pa） Dot Spot Efficiency (in NBS) 比色法 Arrestance (in AFI) 比重法 （inch） （mm） Initial Resistance 初壓損 Final Resistance 末壓損 90~95 > 99 12*24*4 289*595*95 1700 169 324 24*24*4 595*595*95 3400 80~85 > 98 12*24*4 289*595*95 1700 147 324 24*24*4 595*595*95 3400 60~65 > 97 12*24*4 289*595*95 1700 100 324 24*24*4 595*595*95 3400 *Special Sizes are available upon request. ※特殊規格可生產製造。

KJF 206

Material and Service Conditions 材質和使用條件 Type 型式 Description 說明 Construction 總成 Media 濾材 Ultra-Fine Glass Fiber 超細玻璃纖維濾紙 Support Grid 支撐材 Hot Melt Adhesive 熱熔膠 Frame Material 外框材質 Paper Frame 紙框 Metal Frame 金屬框 Frame Type 外框型式 Box Type 箱型 Single Header 單法蘭 Service Conditions 使用條件 The maximum use temperature 使用最高溫度 ℃ 60 The maximum continuous use temperature 連續使用最高溫度 ℃ 40 Instant Highest Humidity 使用瞬間最高濕度 % RH 98（No condensation state） 98（無結露狀態下） 名 稱:康智富科技有限公司 統 編:29168436 地 址:新北市永和區仁愛路141巷30弄26號1樓 電 話:+886-2-29256286 傳 真:+886-2-29256096 E-MAIL :ks.best@msa.hinet.net