|  | KJF207 |
| --- | --- |
|  | ASHRAE Grade V-Cell Extended Surface Air Filter 中性能V-Cell型空氣濾網 Testing Method 測試方法 Dot Spot Efficiency (in NBS Testing Method) 比色法 Arrestance (in AFI Testing Method) 比重法 MERV 90~95% > 99% 14 80~85% > 98% 13 60~65% > 97% 11 By ASHRAE Standard 52.1-1992 (Equal to EN 779) 依ASHRAE 52.1-1992標準 (德國EN 779) By ASHRAE 52.2-1999 Standard 依ASHRAE 52.2-1999標準 Features: ※With More Effective Media Area ※With High Capacity ※With Low Resistance ※With High Dust Collection Capacity ※With Longer Life Span AIRREX V-Cell Air Filter is with multiple mini-pleat media packs and enable to remove air contamination, such as dust, smoke, vapor, soot, pollen, bacteria and etc. The unique V-Type design offers a wide range of efficiency to remove air contamination and provide a very low resistance. V-Cell filter offers high performance and low operating costs; it is ideal for the most difficult operating conditions: ※High Velocity ※Variable Air Volume System ※High Humidity ※Corrosion Environment |

KJF 207

AIRREX V-Cell Air Filter is assembled by eight pieces of mini-pleat packs to compose of four (4) V Types. It contains more media (up to 40%) than standard W-Cell Air Filters. The effective media area results in greater flow capacity, lower resistance, higher dust collection capacity and longer life span. Operating range of Face Velocity is from 0 to 750FPM (0-3.81M/sec) for 12”(292mm) deep units. Efficiency: Per ASHRAE 52.1-1992 standard, the filters have an average atmospheric dust spot efficiency range 60-65%, 80-85% and 90-95% (in NBS Test Method); per ASHRAE 52.2, the efficiency is MERV11, MERV12 & MERV14. Media: V-Cell media is manufactured from water-resistant glass microfiber. The media is pleated from the filter pack and use hot melting glue to replace the traditional aluminum separators. V-Cell media can withstand temperature up to 350ﾟC. The connection between filter face and frame is sealed by fire retardant epoxy, polyurethane foam or silicon to ensure the filter leakage free. Outer Frame: The frame is available for Metal Frame (Galvanized Steel, Aluminum and Stainless Steel) in box type or header type and ABS frame in headed type. V-Cell Air Filter Operating Conditions: ※Recommended Final Pressure Drop: 2.0”w.g. ※Maximum Final Pressure Drop: 3.2”w.g. ※Guaranteed to withstand burst pressure: 6.0”w.g. ※Actual Average Burst Pressure: 10.0” w.g. ※Relative Humidity: 100% 特色：中性能V-CELL型濾網具有多數的迷你褶數濾材，獨特的V型設計 比傳統鋁隔板型的中性能濾網多出40%的濾材面積，可處理較大的風量與較低壓損具有較高的集塵量。 效率：依ASHRAE 52.1-1992標準法測試，濾網具比色法效率60-65%、80-85%、90-95%可供選擇。 濾材：由超細玻纖做成，以上膠間隔方式製成，每個濾網端面與框架銜接處再以耐火環氧樹脂、聚亞氨脂泡沫或矽樹脂，完全密封以確保濾網氣密，防水玻纖濾材能承受溫度到350℃。 外框：框材可選用ABS框、鍍鋅鐵框、鋁框或不銹鋼框。

KJF 207

Performance Data – ASHRAE Grade V-Cell Extended Surface Air Filter 中效率濾網性能表 - V-Cell型空氣濾網 Efficiency Nominal Size Actual Size Rated Capacity Pressure Drop 效率 通稱尺寸 實際尺寸 額定風量 壓力損失 （％） （W*H*D） （W*H*D） （CMH） （Pa） Dot Spot Efficiency (in NBS) 比色法 Arrestance (in AFI) 比重法 （inch） （mm） Initial Resistance 初壓損 Final Resistance 末壓損 90~95 ＞ 99 12*24*12 289*595*292 1700 100 324 24*24*12 595*595*292 3400 80~85 ＞ 98 12*24*12 289*595*292 1700 79 324 24*24*12 595*595*292 3400 60~65 ＞ 97 12*24*12 289*595*292 1700 63 324 24*24*12 595*595*292 3400 *Special Sizes are available upon request. ※特殊規格可生產製造

KJF 207

Material and Service Conditions 材質和使用條件 Type 型式 Description 說明 Construction 總成 Media 濾材 Ultra-Fine Glass Fiber 超細玻璃纖維濾紙 Support Grid 支撐材 Hot Melt Adhesive 熱熔膠 Sealant 密封膠 PU Base Gasket Material 墊片材質 Neoprene Rubber 新平橡膠 Frame Material 外框材質 ABS Frame ABS框 Metal Frame 金屬框 Frame Type 外框型式 Box Type 箱型 Single Header 單法蘭 Service Conditions 使用條件 The maximum use temperature 使用最高溫度 ℃ 60 The maximum continuous use temperature 連續使用最高溫度 ℃ 40 Instant Highest Humidity 使用瞬間最高濕度 % RH (No condensation state) 98（無結露狀態下） 名 稱:康智富科技有限公司 統 編:29168436 地 址:新北市永和區仁愛路141巷30弄26號1樓 電 話:+886-2-29256286 傳 真:+886-2-29256096 E-MAIL :ks.best@msa.hinet.net