|  | KJF301 |
| --- | --- |
|  | High Efficiency Particulate Air Filter – Deep Pleat Type 高效率濾網 – 隔板型 Testing Method 測試方法 Particle Size 粒徑 Efficiency (%) 效率 0.1-0.2um 99.999% above 0.3um 95% 99.97% 99.99% 99.999% By European Standard EN1822 依歐規EN1822標準 *High Temperature Resistant Filter can be option for special use. *依特殊使用性質，可製成耐高溫濾網 The term of “HEPA” filter is defined as the filter to provide a minimum of 95% overall efficiency on thermally generated mono-disperse 0.3 micrometer particles. AIRREX manufactures a complete line of HEPA filter and consists of efficiencies: 95%, 99.97%, 99.99%, 99.999% (EU12 - EU14). The filter provides Standard (STD series) and High (HI series) capacity series. The STD Series HEPA Filter is generally operated at velocities 275 FPM (for depth 11-1/2 inches), 175FPM (for depth 5-7/8 inches); and the HI Series is operated at velocities up to 500FPM (for depth 11-1/2 inches). STD Series HEPA Filter is rated for a max. 220ﾟF temperature use. Temperature up to 750ﾟF can be also available by using optional sealant, gasket and frame. HI Series HEPA Filter is designed to handle higher air flow. Compare to STD Series, HI Series has more pleats and more filtration area. It handles higher air flow with the same resistance. The lower resistance can provide filter longer life span and reduce energy cost. |

KJF301

Each filter is individually tested with thermally generated DOP aerosol. The filter is certified to have a minimum guaranteed efficiency and the results of DOP test are indicated right on the label. This has been the industry standard test method for many years. It is conducted in accordance with EN-1822 using an Auto Scan System to test HEPA efficiency. By measuring the upstream and downstream concentration of these particles, the filter efficiency can be calculated. TDA-33 Leakage Test Equipment can scan to detect the pinhole leaks of HEPA by using liquid aerosol. Features: HEPA media is made of ultra fine glass fiber formed into a 0.038mm thick mat and is pleated to allow a larger surface area to be incorporated within the housing. The media is water-resistant and can withstand temperature up to 500 ﾟC. Deep Pleat Type Air Filter is spaced by corrugated aluminum separators, each separator has at least 0.038mm (0.0015”) thickness. The aluminum should conform to alloy type 5052-H39, 3003-H19, or 1145-H19, of QQ-A-250/11 or ASTM-B209. Corrugated Aluminum Separator: Corrugated aluminum separators maintain uniform spacing between each pleat to allow free flow of air through the filter to ensure all media to have more effective use and increase the strength of filter pack. Both edges of aluminum separators are rolled to prevent media tearing and provide maximum integrity. Rolled edges can decrease the possibility of worker’s hands to be injured during installation. Efficiency: All HEPA filter efficiency is tested in accordance with US MIL-STD-282 (EU Standard) and EN1822. The series provide guarantee efficiency from 95%, 99.97%, 99.99% to 99.999% (EU12-EU14) or H10-H14 (per EN-1822 standard in MPPS Test) on 0.3 micrometer size particles HEPA filter; and 99.999% to 99.999999% or U15-U16 (per EN-1822 standard in MPPS Test) ULPA filter. Media: The ultra-fine glass fiber HEPA media is formed with high density papers. The media is water-resistant and can withstand temperature up to 500℃. Deep Pleat Type can provide more filtration area. Although the filter media is designed to withstand 100% humidity, it is not designed to operate in vapor environment. When the filter exposures to such condition for too long, the filter media will absorb and retain moisture, and thus the filter will be saturated and blocked. As time goes by, filter will fail due to excessive blockage. The function of the filter can be restored by blowing dry air through the filter. Sealant Each media pack is sealed with a special adhesive to ensure the filter media leakage free. Frame: The frame is available for Wooden Frame (High Particle Board Frame) and Metal Frame (Galvanized Steel, Stainless Steel or Aluminum) in Box Type, Double Turn Type or Single Header. Metal faceguard installed on both sides of the filter is available.

KJF301

特色：隔板型濾網以至少0.038mm厚度波褶狀區隔，波褶狀鋁隔板維持每一褶濾紙之等距間隔，氣流易於穿過，確保濾材有效利用及增加強度。鋁隔板雙褶邊防止插破濾紙，提供最大的安全性。另有高風量系列之濾網，因多褶數有較大的過濾面積，於相同壓損下可處理較大的風量。 效率：依歐規EN1822標準測試，即測試濾網之上風處與下風處粒子濃度，HEPA級效率從95~99.999%通過0.3um。 濾材：濾材由超細高密度之玻璃纖維所製成，此濾材耐水且耐溫至攝氏500度，連續性摺以提供高比率之濾材面積，濾網濾材均被特殊密封劑密封，確保濾材四周氣密。 外框：框材可選用木框、鍍鋅鐵框、鋁框或不銹鋼框。可選擇箱型、單法蘭和雙法蘭。濾網兩側可提供加裝金屬護網。

KJF301

High Efficiency Filter Performance Data - Deep Pleat Type HEPA Filter 高效率濾網性能表 - 隔板型濾網 Efficiency Nominal Size Actual Size Rated Capacity Pressure Drop 效率 通稱尺寸 實際尺寸 額定風量 壓力損失 （％） （W*H*D） （W*H*D） （CMH） （Pa） （inch） （mm） Initial Resistance Final Resistance 初壓損 末壓損 Standard Capacity 標準風量 95 12*24*6 305*610*150 850 150 374 24*24*6 610*610*150 1700 12*24*12 305*610*292 1700 237 500 24*24*12 610*610*292 3400 99.97 99.99 12*24*6 305*610*150 600 250 500 24*24*6 610*610*150 1200 24*48*6 610*1220*150 2380 12*24*12 305*610*292 950 24*24*12 610*610*292 1900 High Capacity 高風量 99.97 99.99 12*24*12 305*610*292 1700 336 500 24*24*12 610*610*292 3400 * Special Sizes are available upon request. ※特殊規格可生產製造

KJF301

Material and Service Conditions 材質和使用條件 Type 型式 Description 說明 Construction 總成 Media 濾材 Ultra-Fine Glass Fiber 超細玻璃纖維濾紙 Support Grid 支撐材 Corrugated Aluminum Separators 波浪隔板 Sealant 密封膠 PU BASE Gasket Material 墊片材質 Neoprene Rubber 新平橡膠 Frame Material 外框材質 Wooden Frame 木框 Metal Frame 金屬框 Frame Type 外框型式 Box Type 箱型 Single Header or Double Turn Type 單法蘭 or 外摺框 Service Conditions 使用條件 The maximum continuous use temperature 連續使用最高溫度 ℃ 60 Instant Highest Humidity 使用瞬間最高濕度 % RH 100 ( No condensation state) 100（無結露狀態下） 名 稱:康智富科技有限公司 統 編:29168436 地 址:新北市永和區仁愛路141巷30弄26號1樓 電 話:+886-2-29256286 傳 真:+886-2-29256096 E-MAIL :ks.best@msa.hinet.net