|  | KJF302 |
| --- | --- |
|  | High Efficiency Particulate Air Filter (HEPA/ULPA) – Mini Pleat Panel Type 高效率及超高效濾網–平板型 (HEPA/ULPA) Testing Method 測試方法 Particle Size 粒徑 Efficiency (%) 效率 0.3um 95% 99.97% 99.99% 99.999% 0.1-0.2um 99.999% above By European Standard EN1822 依歐規EN1822標準 Features: No Corrugated Aluminum Separators High Efficiency and Low Pressure Drop Allow Great Amount of Media in Shallow Depth The air flow, initial resistance and dust collection capacity of the Mini Pleat Series media w/55mm pack is much better than conventional HEPA filter which is made with corrugate aluminum separators and with a 150mm deep. For handling large air volume, the operation cost becomes a prime consideration in a typical clean room application. One of the most important is to evaluate the Pressure Drop of HEPA due to Pressure losses of HEPA will be consumed the most energy in any clean room. AIRREX Mini Pleat HEPA/ULPA Filter is designed for extending filter’s life span and decreasing the pressure drop. Mini Pleat series filter is suitable for clean room, workstations and benches FFU use. |

KJF302

Efficiency: All HEPA filter efficiency is tested in accordance with US MIL-STD-282 (EU Standard) and EN1822. The series provide guarantee efficiency from 99.97%, 99.99% to 99.999% (EU12-EU14) or H10-H14 (per EN-1822 standard in MPPS Test) on 0.3 micrometer size particles HEPA filter; and 99.999% to 99.999999% or U15-U16 (per EN-1822 standard in MPPS Test) on 0.1 – 0.2 micrometer size particles ULPA filters.. Media: HEPA media is made from ultra fine glass fiber formed with high density papers. Use hot melting glue to replace traditional aluminum separators. Each pleat is spaced by hot-melt adhesive to allow air flow through the filter with minimum resistance. Inside of frame to be sealed by sealant to prevent filter media leakage. Frame: The filter media pack is permanently bonded with epoxy or PU to an anodized aluminum extruded frame or wood board frame. Aluminum extruded frame can increase strength and rigidity for corrosion resistance 特色：平板型濾網提供多種的配置適用於無塵室、無塵工作站、無菌操作台及風車濾網組等嚴格的潔淨需求，迷你摺數系列的濾網過濾之風量、初壓損及集塵量效果較隔板型之HEPA濾網好很多，迷你摺數設計意在延長濾網使用壽命及降低壓損。因產業特性需求在耗材的選用上，本公司亦可提供低硼濾材，製造符合客戶需求之終端濾網。 效率：依歐規EN1822標準測試，即測試濾網之上風處與下風處粒子濃度，HEPA級效率從95~99.999%通過0.3um，ULPA級效率從99.999~99.999999%通過0.1~0.2um。 濾材：濾材由超細玻璃纖維經褶疊組裝入框架內，濾紙經由熱熔膠間隔，不會釋出化學性污染到無塵室，使空氣以最低的壓損通過濾網。 外框：外框內側四周以密封膠密封，防止濾材空隙及洩漏。鋁擠外框經陽極處理增加強硬度及耐久的防腐性。以PU膠密封於鋁擠型框架達到完全的氣密無洩漏。.

KJF302

High Efficiency Filter Performance Data - Mini Pleat Panel Type (HEPA/ULPA) 高效率及超高效率濾網性能表 - 平板型濾網 Efficiency Nominal Size Actual Size Rated Capacity Initial Resistance 效率 通稱尺寸 實際尺寸 額定風量 初壓損 （W*H*D） （W*H*D） （％） （inch） （mm） （CMH） (Pa) 99.97 99.99 24*24*2 570*570*50 400 87 610*610*50 75 24*24*3 570*570*65 450 99 610*610*65 85 24*48*2 570*1170*50 800 82 610*1220*50 75 24*48*3 570*1170*65 900 93 610*1220*65 82 48*48*2 1170*1170*50 1800 88 1220*1220*50 81 48*48*3 1170*1170*65 2000 97 1220*1220*65 89 99.9995 （5N5） 24*24*2 570*570*50 400 91 610*610*50 79 24*24*3 570*570*65 450 103 610*610*65 89 24*48*2 570*1170*50 800 86 610*1220*50 79 24*48*3 570*1170*65 900 97 610*1220*65 86 48*48*2 1170*1170*50 1800 92 1220*1220*50 85 48*48*3 1170*1170*65 2000 101 1220*1220*65 93 *Special Sizes are available upon request. ※特殊規格可生產製造。

KJF302

Efficiency Nominal Size Actual Size Rated Capacity Initial Resistance 效率 通稱尺寸 實際尺寸 額定風量 初壓損 （W*H*D） （W*H*D） （％） （inch） （mm） （CMH） (Pa) 99.99995 （6N5） 24*24*2 570*570*50 400 97 610*610*50 83 24*24*3 570*570*65 450 109 610*610*65 97 24*48*2 570*1170*50 800 91 610*1220*50 81 24*48*3 570*1170*65 900 103 610*1220*65 92 48*48*2 1170*1170*50 1800 98 1220*1220*50 90 48*48*3 1170*1170*65 2000 109 1220*1220*65 100 *Special Sizes are available upon request. ※特殊規格可生產製造。 名 稱:康智富科技有限公司 統 編:29168436 地 址:新北市永和區仁愛路141巷30弄26號1樓 電 話:+886-2-29256286 傳 真:+886-2-29256096 E-MAIL :ks.best@msa.hinet.net

KJF302

Material and Service Conditions 材質和使用條件 Type 型式 Description 說明 Construction總成 Media 濾材 Ultra-Fine Glass Fiber Filter Paper 超細玻璃纖維濾紙 Support Grid 支撐材 Hot Melt Adhesive 熱熔膠 Sealant 密封膠 PU BASE Gasket Material 墊片材質 Neoprene Rubber 新平橡膠 Gasket Location 墊片位置 None 無 Upstream上風 Downstream下風 Both Sides 兩側 Frame Type 外框類型 Gasket Type 乾式 Jel Type 濕式 Frame Material 外框材質 Anodized Extruded Aluminum 鋁框陽極處理 Face Guard Material 保護網材質 Expanded Galvanized Metal 擴張烤漆鐵網 Anodized Extruded Aluminum 擴張陽極處理鋁網 Face Guard Location 保護網位置 None 無 Upstream 上風 Downstream下風 Both Sides 兩側 Service Conditions 使用條件 The maximum continuous use temperature 連續使用最高溫度 ℃ 60 Instant Highest Humidity 使用瞬間最高濕度 % RH 100 ( No condensation state) 100（無結露狀態下） 名 稱:康智富科技有限公司 統 編:29168436 地 址:新北市永和區仁愛路141巷30弄26號1樓 電 話:+886-2-29256286 傳 真:+886-2-29256096 E-MAIL :ks.best@msa.hinet.net