|  | KJF303 |
| --- | --- |
|  | High Efficiency Particulate Air Filter (HEPA/ULPA) - Mini Pleat V Type 高效率濾網–V型 (HEPA/ULPA) Testing Method 測試方法 Particle Size 粒徑 Efficiency (%) 效率 0.3um 95% 99.97% 99.99% 99.999% 0.1-0.2um 99.999% above By European Standard EN1822 依歐規EN1822標準 Features: *More Effective Media Area *High Capacity *Low Resistance *Long Life Span AIRREX V-HEPA or V-ULPA filter is assembled by multiple mini-pleat packs formed into six to eight pieces of V type pleat. It contains more media (up to 90%) than standard W- HEPA filter, can easily remove air contamination such as fine dust, smoke, vapor, soot, pollen, bacteria and etc. The effective media area results in greater flow capacity, lower resistance, and longer life span. With high capacity, low pressure drop & longer life span advantages, can be used to replace the traditional aluminum separators filters. |

KJF303

Efficiency: All HEPA filter efficiency is tested in accordance with US MIL-STD-282 (EU Standard) and EN1822. By measuring the upstream & downstream particle concentration, the series provide guarantee efficiency from 95%, 99.97%, 99.99% to 99.999% (EU12-EU14) or H10-H14 (per EN-1822 standard in MPPS Test) on 0.3 micrometer size particles HEPA filter; and 99.999% to 99.999999% or U15-U16 (per EN-1822 standard in MPPS Test) ULPA filter. Media: V-HEPA media is made from glass microfiber. It is water resistant and can withstand temperature up to 350 ﾟC. Use hot melting glue to replace traditional aluminum separators. The V-HEPA media is manufacture from glass microfiber. It is water resistance and can withstand temperature up to 350℃. The filter media is folded into mini-pleats and spaced by hot melting glue to ensure a best pleating geometry. Each media pack and frame end is completely sealed by fire-retardant epoxy, polyurethane foam or silicon sealant to ensure leakage free in a clean room. Frame: The frame is available for Metal Frame (Galvanized Steel, Aluminum, Particleboard and Stainless Steel) in Box Type or Header type 特色：V型設計具有多數的迷你褶數濾材，比傳統型的濾網多90%的濾材面積，大的過濾面積可處理較大的風量與較低壓損和較長的使用壽命。 效率：依歐規EN1822標準測試，即測試濾網之上風處與下風處粒子濃度，HEPA級效率從95~99.999%通過0.3um，ULPA級效率從99.999~99.999999%通過0.1~0.2um。 濾材：濾材由超細玻璃纖維經褶疊組裝入框架內，濾紙經由熱熔膠間隔，不會釋出化學性污染到無塵室。 外框：框材可選用鍍鋅鐵框、鋁框或不銹鋼框。可選擇箱型、單法蘭和雙法蘭。濾網兩側可提供加裝金屬護網。

KJF303

High Efficiency Filter Performance Data - Mini Pleat V Type 高效率濾網性能表 –V型濾網 Efficiency Nominal Size Actual Size Rated Capacity Pressure Drop 效率 通稱尺寸 實際尺寸 額定風量 壓力損失 （％） （W*H*D） （W*H*D） （CMH） （Pa） （inch） （mm） Initial Resistance 初壓損 Final Resistance 末壓損 99.97 99.99 12*24*12 287*592*292 1500 250 500 24*24*12 592*592*292 3000 12*24*12 305*610*292 1700 24*24*12 610*610*292 3400 *Special Sizes are available upon request. ※特殊規格可生產製造。

KJF303

Material and Service Conditions 材質和使用條件 Type 型式 Description 說明 Construction總成 Media 濾材 Ultra-Fine Glass Fiber 超細玻璃纖維濾紙 Support Grid 支撐材 Hot Melt Adhesive 熱熔膠 Sealant 密封膠 PU BASE Gasket Material 墊片材質 Neoprene Rubber 新平橡膠 Frame Material 外框材質 Metal Frame 金屬框 Frame Type 外框型式 Box Type 箱型 Single Header 單法蘭 Service Conditions使用條件 The maximum continuous use temperature 連續使用最高溫度 ℃ 60 Instant Highest Humidity 使用瞬間最高濕度 % RH 100 ( No condensation state) 100（無結露狀態下） 名 稱:康智富科技有限公司 統 編:29168436 地 址:新北市永和區仁愛路141巷30弄26號1樓 電 話:+886-2-29256286 傳 真:+886-2-29256096 E-MAIL :ks.best@msa.hinet.net