|  | KJF601 |
| --- | --- |
|  | Indoor Replaceable Filter Housing 室內可更換型濾網箱組 Testing Method 測試方法 Particle Size 粒徑 Efficiency (%) 效率 0.3um 95% 99.97% 99.99% 99.999% 0.1-0.2um 99.999% above By European Standard EN1822 依歐規EN1822標準 Feature: AIRREX develops latest HEPA housing made by anodized extruded aluminum to substitute traditional heavy and expensive metallic surface trim housing. It can reduce user’s operation cost. HEPA housings are for ceiling grid at clean room use or T grid use. Filter can be easily to replace or install at clean room. Base on classes of clean room to choose HEPA or ULPA filters Compare with module type HEPA filters, end user is not necessary to replace entire box, but only need to replace new HEPA/ULPA; investment cost could be reduced a lot. Efficiency: According to European Standard EN1822, by testing the particle concentration of upstream & downstream area, efficiency is from 99.99% to 99.999% @0.3 micron (H13-14) size particles HEPA filter; and 99.999% - 99.999999% @ 0.1-0.2 micron (U15-U17) size particles ULPA filter. |

KJF601

Media: HEPA media is made from ultra fine glass fiber formed with high density papers. Each pleat is spaced by hot-melt adhesive to allow air flow through the filter with minimum resistance. Housing Material: Anodized Extruded Aluminum. Inlet size is available for 8”-14”. Total Height is 150 mm excluding of the height of Inlet. Height of Inlet is 80mm. Material of upper casing is 1.0mm thickness Painted Steel. 特色： 終端拋棄型箱組設計用於無塵室乾式天花板骨架或濕式天花板骨架系統。於室內更換濾網，安裝簡便。濾網可依客戶需要彈性設計，可選擇摺紙厚度、濾材效率、風量及入風口尺寸，無塵室設計者能配置使用量以執行符合規格及運轉成本。依無塵室等級，可選用HEPA或ULPA等濾網。 效率： 依歐規EN1822標準測試，即測試濾網之上風處與下風處粒子濃度，HEPA級效率從95~99.999%通過0.3um，ULPA級效率從99.999~99.999995%通過0.1~0.2um。 濾材： 濾材由超細玻璃纖維經褶疊組裝入框架內，濾紙經由熱熔膠間隔，不會釋出化學性污染到無塵室，使空氣以最低的壓損通過濾網。 箱體： 材質為陽極處理鋁擠型，上蓋材質為1.0mm厚鐵烤漆，箱體高度150mm(不含入風口高度)，入風口高度尺寸80mm。

KJF601

Performance Data – Indoor Replaceable Filter Housing (HEPA/ULPA) 室內可更換型濾網箱組性能表 - 高效率及超高效率濾網 Efficiency Housing Size Filter Size Rated Capacity Initial Resistance Particle size 效率 箱體尺寸 濾網尺寸 額定風量 初壓損 粒徑 （W*H*D） （W*H*D） （％） （mm） （mm） （CMH） (Pa) （um） 99.97 99.99 570*570*150 528*528*80 350 100 0.3 600*600*150 558*558*80 88 570*1170*150 528*1128*80 800 101 600*1210*150 558*1168*80 91 99.9995 (5N5) 570*570*150 528*528*80 350 104 0.1~0.2 600*600*150 558*558*80 92 570*1170*150 528*1128*80 800 104 600*1210*150 558*1168*80 96 *Special Sizes are available upon request. ※特殊規格可生產製造。 Material and Service Conditions 材質和使用條件 Type 型式 Description 說明 Construction 總成 Media 濾材 Ultra-Fine Glass Fiber Filter Paper 超細玻璃纖維濾紙 Support Grid 支撐材 Hot Melt Adhesive 熱熔膠 Sealant 密封膠 PU BASE Gasket Material 墊片材質 Neoprene Rubber 新平橡膠 Gasket Location 墊片位置 None 無 Upstream上風 Downstream下風 Both Sides 兩側

KJF601

Construction 總成 Housing Type 外框類型 Gasket Type 乾式 Housing Material 外框材質 Anodized Extruded Aluminum 鋁框陽極處理 Face Guard Material 保護網材質 Expanded Painted Steel Metal 擴張烤漆鐵網 Anodized Extruded Aluminum Metal 擴張陽極處理鋁網 Face Guard Location 保護網位置 None 無 Upstream 上風 Downstream 下風 Both Sides 兩側 Inlet Size 入風口尺寸（inch） 8 10 12 14 Inlet Height 入風口高度（mm） 80 Insulation Material 保溫材質 PE Insulation Thickness 保溫厚度（mm） None 無 10 25 Service Conditions 使用條件 The maximum continuous use temperature 連續使用最高溫度 ℃ 60 Instant Highest Humidity 使用瞬間最高濕度 % RH 100 ( No condensation state) 100（無結露狀態下） 名 稱:康智富科技有限公司 統 編:29168436 地 址:新北市永和區仁愛路141巷30弄26號1樓 電 話:+886-2-29256286 傳 真:+886-2-29256096 E-MAIL :ks.best@msa.hinet.net