|  | KJF602 |
| --- | --- |
|  | Terminal Filter Modules (Mini Pleat Series) 終端拋棄型濾網箱組 Testing Method 測試方法 Particle Size 粒徑 Efficiency (%) 效率 0.3um 95% 99.97% 99.99% 99.999% 0.1-0.2um 99.999% above By European Standard EN1822 依歐規EN1822標準 Feature: High Quality Construction in a Highly Versatile Design. Terminal Filter Modules are designed for standard T- bar ceiling grids or Gel seal ceiling grid system use. It's easy and simple to install and maintain these thin and lightweight units. The module can be flexibly designed to meet customer spec’s demand. By selecting among pack depth, media efficiency, air capacity and inlet size, the clean room designer can configure the unit to meet spec requirements and operating cost. Depending on the number of units used in the ceiling, the rate of air recirculation and clean room overall design, Airrex Terminal Filter Modules is able to provide cleanliness levels from Class 1 to Class 100,000. |

KJF602

The unique Benefits: ※ To eliminate the concern of air blockage is better than Deep Pleat Type Air Filer. ※ With Anticorrosive and Anodized Extruded Aluminum Housing Construction. ※ Four (4) suspending holes to provide seismic protection and reduce the stress load of grid. ※ Dimpled inlet collars help to secure the HVAC ductwork and prevent slippage. ※ 100% quality control- every unit is tested and certified to meet efficiency and pressure drop requirements. Factory Testing Airrex tests all terminal filter modules to be in accordance with the International Environmental Science recommended particles standard. Test result including of penetration value (%) and pressure drop (inch/w.g.) will be recorded on filter label and carton label. Capacity vs Pressure Drop The EN 1822 Test Machine examines each filter's Capacity vs. Pressure Drop. Capacity test is according to volumetric parameters, i. e., 100 CFM per square foot of filter face area, which is an expression of the volume of air moving through the filter. Scan Test In addition to the efficiency test and penetration test, by using a laser particle counter to scan each filter surface and edge to examine any pinhole leakage. Readings greater than 0.01% of the upstream concentration are determined as unacceptable; the filter must be rejected or repaired and retested. Efficiency: According to European Standard EN1822, by testing the particle concentration of upstream & downstream area, efficiency is from 99.99% to 99.999% @0.3 micron (H13-14) size particles HEPA filter; and 99.999% - 99.999999% @ 0.1-0.2 micron (U15-U17) size particles ULPA Filter. Media: Media is made from ultra fine glass fiber formed with high density papers. Each pleat is spaced by hot-melt adhesive to allow air flow through the filter with minimum resistance. Housing Material: Anodized Extruded Aluminum construction. Inlet size is available for 8”-14”. Total Height is 150 mm excluding of the height of Inlet. Height of Inlet is 80mm. Material of upper casing is 1.0mm thickness Painted Steel.

KJF602

特色：終端拋棄型箱組設計用於無塵室乾式天花板骨架或濕式天花板骨架系統。安裝及維修既簡單又平整。濾網可依客戶需要彈性設計，可選擇摺紙厚度、濾材效率、風量及入風口尺寸，無塵室設計者能配置使用量以執行符合規格及運轉成本。依據此型濾網使用於天花板之數量，空氣之循環率和整體的無塵室設計，此層流濾網能提供潔淨標準從潔淨度1到100,000。 效率：依歐規EN1822標準測試，即測試濾網之上風處與下風處粒子濃度，HEPA級效率從95~99.999%通過0.3um，ULPA級效率從99.999~99.999995%通過0.1~0.2um。 濾材：濾材由超細玻璃纖維經褶疊組裝入框架內，濾紙經由熱熔膠間隔，不會釋出化學性污染到無塵室，使空氣以最低的壓損通過濾網。 箱組：材質為陽極處理鋁擠型，上蓋材質為1.0mm厚鐵烤漆，箱體高度130mm(不含入風口高度)，入風口高度尺寸80mm。

KJF602

Performance Data – Terminal Filter Modules (Mini Pleat Series) 終端拋棄型濾網箱組性能表 - 高效率及超高效率濾網 Efficiency Nominal Size Actual Size Rated Capacity Initial Resistance Particle size 效率 通稱尺寸 實際尺寸 額定風量 初壓損 粒徑 （W*H*D） （W*H*D） （％） （inch） （mm） （CMH） (Pa) （um） 99.97 99.99 24*24 570*570*140 450 103 0.3 600*600*140 92 24*48 570*1170*140 900 97 600*1210*140 87 99.9995 (5N5) 24*24 570*570*140 450 108 0.1~0.2 600*600*140 96 24*48 570*1170*140 900 101 600*1210*140 93 * Special Sizes are available upon request. ※特殊規格可生產製造。 Material and Service Conditions 材質和使用條件 Type 型式 Description 說明 Construction 總成 Media 濾材 Ultra-Fine Glass Fiber Filter Paper 超細玻璃纖維濾紙 Support Grid 支撐材 Hot Melt Adhesive 熱熔膠 Sealant 密封膠 PU BASE Gasket Material 墊片材質 Neoprene Rubber 新平橡膠 Gasket Location 墊片位置 Non 無 Downstream 下風

KJF602

Material and Service Conditions 材質和使用條件 Construction 總成 Housing Type 外框類型 Gasket Type 乾式 Housing Material 外框材質 Anodized Extruded Aluminum 鋁框陽極處理 Face Guard Material 保護網材質 Expanded Painted Steel Metal 擴張烤漆鐵網 Anodized Extruded Aluminum Metal 擴張陽極處理鋁網 Face Guard Location 保護網位置 Downstream 下風 Inlet Size 入風口尺寸（inch） 8 10 12 14 Inlet Height 入風口高度（mm） 70 Insulation Material 保溫材質 PE Insulation Thickness 保溫厚度（mm） None 無 10 25 Service Conditions 使用條件 The maximum continuous use temperature 連續使用最高溫度 ℃ 60 Instant Highest Humidity 使用瞬間最高濕度 % RH 100 ( No condensation state) 100（無結露狀態下） 名 稱:康智富科技有限公司 統 編:29168436 地 址:新北市永和區仁愛路141巷30弄26號1樓 電 話:+886-2-29256286 傳 真:+886-2-29256096 E-MAIL :ks.best@msa.hinet.net