|  | KJF603 |
| --- | --- |
|  | Fan Filter Unit (F.F.U.) 風車濾網箱組 FFU is short for Fan Filter Unit which is consisted of Fan Unit and a Mini Pleat HEPA/ULPA Filter with efficiency 99.99% - 99.999995%. F.F.U.：Fan Filter Unit風車濾網組簡稱 第一部分：FAN UNIT，送風機。 第二部份：FILTER，濾網，可搭配HEPA或ULPA，效率99.99% ~ 99.999995%。 F.F.U. Advantages: 1. Can filter system terminal equipment; cleanliness level is from Class 1 to 100K. 2. Modular: Easy deployment location, and may increase or decrease by the number of FFU in order to meet the clean environment a Relayout needs. 3. Adjustable Air Flow: By controlling the motor speed to adjust air flow, the clean room laminar flow (unidirectional flow) are very help. 4. Widely Used: Clean Room factory side, device-side….can be applied. F.F.U.使用優點: 過濾系統終端設備：可達CLASS 1~100K潔淨等級。 模組化：容易調配位置、增減F.F.U.數量符合潔淨環境 RELAYOUT需求。 可調整風量：藉由控制馬達轉速調整風量，對於潔淨室層 流有相當幫助。 廣泛應用：無塵室厰務端、設備端…都可以加以應用。 |

KJF603

KJF CLEAN F.F.U. features: KJF CLEAN.特點 1. Motor: KJF CLEAN FFU used Germany-made External Rotor Motor. 馬達：KJF CLEAN F.F.U.選用德制外轉子馬達。 1-1.：External Rotor Motor, the fan with the motor rotation. 外轉子馬達，風扇隨馬達轉動。 1-2.：High Reliability, Stable Operation. 高信賴度，運轉穩定。 1-3.：High Static Pressure, prolong the service life of FFU. 高靜壓，有效延長業主F.F.U.使用年限。 1-4.：Excellent Cooling Capacity, airflow through motor, reduce the failure probability. 散熱能力優異，氣流經過馬達，降低故障機率。 1-5.：Balancing Excellence, bearing shorter than traditional motors. 動平衡優異，軸承較傳統馬達短。 Motor Fans: Airrex FFU used 3D design backward fans, motor fan (blades) difficult to attach the dust. 風扇：Airrex F.F.U.選用3D設計後傾式風扇，風扇葉片不易附著粉塵。 Adjustable air volume flow: 風量可調整： 3-1： AC Series FFU is available with 3 speeds control model, 5 speeds control model or continuous speed control model to adjust FFU air volume flow. AC F.F.U.可以三段、五段或無段調速。 3-2.：EC Series F.F.U. used EBM BUS System. The air volume flow of each EC Series F.F.U. can be controlled locally or remotely. Each unit can be independently operated and controlled; or a group of EC Series F.F.U. can be operated and controlled together as a system. The EBM BUS system can control up to 7936 units of EC Series F.F.U. This system is accurate, easy to use and provide maximum flexibility for future expansion. EC F.F.U.採用EBM BUS系統，可以群組或各台方式直接控制調整FFU風量，並遠端控制馬達轉速. 系統操作簡便, 擴充性極佳可擴充至7936台。

KJF603

Power Supply: 電源輸入 4-1.：AC Type – Single Phase, 220-230V, 50 or 60 Hz. Use ring type transformer to reduce noise and eddy current, i.e. less energy loss. AC- 1ψ220~230V 50~60Hz，採環式變壓器，可減少電源部份噪音可形成較完美的電源輸入曲線降 低馬達耗損。 4-2.：EC Type – Single Phase, 220-230V, 50 or 60 Hz. Use a 500W variable speed controller to control the motor rpm according to an external analogue input (pressure, temperature settings etc..). DC motors consumes 40-60% energy less than AC motors, thus DC motors run with less noise and less temperature rise. EC - 1ψ220~230V 50~60Hz，採500W電子整流器無段變速可利用外在參數（壓力、溫度等訊號）控制轉數或利用電腦直接輸入。直流馬達可比交流馬達節省40~60%的耗電量，運轉時也較安靜、溫度較低。 Filter Efficiency: According to European Standard EN1822, by testing the particle concentration of upstream & downstream area, efficiency is from 99.99% to 99.999% @0.3 micron (H13-14) size particles HEPA filter; and 99.999% - 99.999999% @ 0.1-0.2 micron (U15-U17) size particles ULPA filter. 濾網：歐規EN1822標準測試，即測試濾網之上風處與下風處粒子濃度，HEPA級效率從95~99.999%通過0.3um，ULPA級效率從99.999~99.999995%通過0.1~0.2um。 Media: Media is made from ultra fine glass fiber formed with high density papers. Each pleat is spaced by hot-melt adhesive to allow air flow through the filter with minimum resistance. 濾材：濾材由超細玻璃纖維經褶疊組裝入框架內，濾紙經由熱熔膠間隔，不會釋出化學性污染 到無塵室，使空氣以最低的壓損通過濾網。 Housing Material: Stainless Steel or Anodized Extrude Aluminum Housing. 箱體材質：為不鏽鋼、鍍鋅鋁。 HEPA or ULPA Filter’s pressure drop can be lower to meet special design requirement. AIRREX可依業主需求設計低壓損HEPA、ULPA FILTER，使F.F.U.提供較大機外靜壓，以符合 特殊設計需求。

KJF603

KJF603

Testing Method 測試方法 Particle Size 粒徑 Efficiency (%) 效率 0.3um 95% 99.97% 99.99% 99.999% 0.1-0.2um 99.999%以上 By European Standard EN1822 依歐規EN1822標準

KJF603

Fan Filter Unit (F.F.U) Performance Data – HEPA/ULPA Filter 風車濾網箱組性能表 - 高效率及超高效率濾網 Efficiency Housing Size Filter Size Rated Capacity Initial Resistance Particle size 效率 箱體尺寸 濾網尺寸 額定風量 初壓損 粒徑 （W*H*D） （W*H*D） （％） （mm） （mm） （CMH） (Pa) （um） 99.97 99.99 570*570*250 570*570*50 400 87 0.3 570*570*65 450 99 570*1170*250 570*1170*50 800 82 570*1170*65 900 93 99.9995 (5N5) 570*570*250 570*570*50 400 91 0.1~0.2 570*570*65 450 103 570*1170*250 570*1170*50 800 86 570*1170*65 900 97 * Special Sizes are available upon request. ※特殊規格可生產製造。